## BHARAT SANCHAR NIGAM LIMITED

(A Govt. of India Enterprise)

O/o The Telecom District Manager, Bolangir- 767001

TECHNICAL BID

TENDER PAPER FOR CARRYING OUT EARTHING WORKS IN DIFFERENT TELEPHONE EXCHANGES & BTS PREMISES

OF BOLANGIR TELECOM DISTRICT

NIT No: W-78/10-11/08 Dated at Bolangir on the 16th June, 2010.

| ISSUED TO ( Name & Address of the Bidder ) | Signature with Seal of the Issuing Authority and date of issue |
| --- | --- |

O/o the Telecom District Manager,

Door Sanchar Bhawan,

Bolangir- 767001

Tel – (+91) 6652 – 234001, 234500 (F)

NIT No: W-78/10-11/08			                       Dated at Bolangir on the 16th June, 2010.

NOTICE  INVITING TENDER

Properly WAX/PVC sealed tenders in the prescribed  form are invited by the Telecom. District Manager, BSNL, Telecom District ,  Bolangir, from bonafide and reputed institution/ firms/ contractors  for carrying out   Earthing  work  at  different  telephone exchanges and BTS premises of Bolangir Telecom District.

| Sl. No. | Description | Cost of Tender Paper | Approximate Estimate Cost | EMD |
| --- | --- | --- | --- | --- |
|  | Carrying out Earthing work at different telephone exchanges and BTS premises of Bolangir Telecom District. | Rs.520/- | Rs.12,00,000/- | Rs.30,000/- |

Eligibility Criterion for the above works: -

The contractor should have experience of having done the  Earthing  work in BSNL/MTNL/State Govt./ Central Govt. or central  PSUs of amount not less than Rs 2, 00, 000/- (Rupees Two Lakhs) during last two FY 2008-09  and 2009-10. Experience certificate in this regard is to be issued by an officer not below the rank of Deputy General Manager or equivalent. The intending bidder should also  possess the following documents to become eligible for participating in the tender.

- EPF Registration Certificate

- Service Tax registration No.

- Contractor license

- Valid Central Labor License or undertaking  to submit the same within one month from date of agreement

Tender papers can be had from SDE(NW. Plg.-CFA.), O/o the TDM, Bolangir on payment of Rs.520/- towards the cost of tender paper in shape of Cash deposited with the AO(Cash), BSNL, O/o the TDM, Bolangir or DD from any scheduled bank at Bolangir in favour of A.O.(Cash), BSNL, O/o The Telecom District Manager, Bolangir. Bidders may also download the tender form from website (www.orissa.bsnl.co.in) and enclose the DD as stated above along with it.

| Sale of Tender Paper | Last date of submission | Tender document to be dropped at | Time and date of Opening of tender |
| --- | --- | --- | --- |
| From 18/06/2010 to 01/07/2010 during office hours i.e. 10:30 hrs to 17:30 hrs. | Upto 13:00 hrs of Dt.02/07/2010 | Tender Box available in the chamber of AGM(CM), O/o TDM, Bolangir | 16: 00 hrs of Dt.02/07/2010. |

The detailed terms and conditions, EMD particulars etc. are available in the tender documents. Tenders without EMD will be rejected. No exemption Cost of Tender Documents and EMD under NSIC is permitted.TDM, Bolangir reserves the right to reject or accept any or all the tenders without assigning any reasons whatsoever and is not bound to accept the lowest tender. The sealed tenders can be dropped in the tender box available in the chamber of AGM (CM),  O/o TDM, Bolangir on or before the date & time mentioned above. The tender documents can also be sent through registered post or courier in the address of AGM(CM) of this office. BSNL Bolangir will not be responsible for any kind of non-delivery or late delivery of tender documents. The tenders received after the due date and time will be summarily rejected.

Telecom District Manager

Bolangir

TENDER FOR CARRYING OUT EARTHING WORK  IN DIFFERENT TELEPHONE EXCHANGES & BTS PREMISES OF BOLANGIR TELECOM DISTRICT

### OFFICE OF THE TELECOM DISTRICT MANAGER, BOLANGIR

TABLE OF CONTENTS

SERIAL NO.	CONTENT	PAGE NO.

Technical Bid Document

1.	Notice Inviting Tender	1

2.	Tenderer’s Profile	3

3.	Definations	4

4.	General Terms & Conditions	5

5.	Bid Security	6

6.	Documents to be submitted	7

7.	Performance  Security	8

8.	Labor Welfare Measures	9

9.	Termination of Contract	9

10.	Payment Terms  & Conditions	10

11.	Warranty	11

12.	Technical Specifications	11-13

13.	Instructions to Contractor	13

14.	Diagrams	14-15

15.	Proforma of Agreement (Annexure-II)	16

16.	Proforma of No near relative working in BSNL (Annexure-III)	17

17.	Proforma of Letter of Authorization (Annexure-IV)	18

Financial Bid Document

18.	Financial Bid (Annexure-V)	20

19.	Check List	21

# ANNEXURE – I

# TENDERER’S PROFILE

1.	Full name of firm	_____________________________________

(In capital letters)	________________________________________

2.	Firm’s Address	_____________________________________

______________________________________

3.	Telephone Number(s)	_____________________________________

(Landline & Mobile)

4.	Is the firm proprietary or	________________________________________

Partnership?

5.	Name(s) of the Proprietor or	________________________________________	Partners.

6.	Income tax Account (PAN) No.	________________________________________	(Attach current return filed copy)

7.	Details of past works done	________________________________________

with State/Central Govt. (If any)

8.	Experience Certificate (Attach proof)	________________________________________

9.	Contractor Registration No. (If any)	________________________________________

With class (Attach proof)

10.	EPF Number	________________________________________

11.	ESI Number	________________________________________

I/ We hereby certify that the above mentioned particulars are true and correct.

Place:       	(Signature of Tenderer with Seal)

Capacity in which signing

Date:

SECTION - I

1.	DEFINITIONS

(A)	The definition of terms used in this document are as follows:

i)           BSNL :BSNL means Bharat Sanchar Nigam Limited   a Government of India Enterprise under  Ministry of  Communication and IT.

ii)	Department: Department means BSNL

iii)	The SSA Head: Means the head of  Bolangir  Telecom District , designated as Telecom District Manager, Balangir and his successors.

iv)	The jurisdiction of the SSA Head: The jurisdiction of the Telecom District Manager	means the Balangir Telecom District which Coincides geographically with Balangir & Sonepur Revenue District.

iv)	Representative of the SSA Head:Representative of Telecom District Manager means Officer and staff for the time being deputed by the Telecom District Manager for inspecting or supervising the work or testing etc.

v)	Contract : The term contract means the document forming the tender and acceptance thereof and the formal agreement executed between the competent authority on behalf of the BSNL , Balangir and the contractor, together with the documents referred to therein including these conditions, the specifications, designs, drawings and instructions issued from time to time, by the engineer in-charge and all these documents taken together shall be deemed to form one contract and shall be complementary to one another. In the contract, the following expressions shall, unless the context otherwise requires, have the meanings, hereby respectively assigned to them. The expression works or work shall unless there be something either in the subject or context repugnant to such construction, be construed and taken to mean the works by or by virtue of the contract contracted to be executed whether temporary or permanent and whether original, altered, substituted or additional.

vi)	Contractor: The contractor shall mean, the individual, firm or company, whether incorporated or not, undertaking the works and shall include the legal personal representative of such individual or the persons composing such firm or company, or the successors of such firm or company and the permitted assignees of such individual, firm or company.

vii)	“The Work Order” means the order issued by the BSNL, Bolangir  to the Bidder  including all      attachments & appendices thereto and all document incorporated by reference therein. The work order shall be deemed as “Contract” appearing in the document.

viii)	 “The Contract Price” means the price payable to the bidder under the contract  for  proper performance of its contractual obligations.

ix)	Site: The site shall mean the land / or other places on, where work is to be executed under the contract or any adjacent land, path or street through which, the work is to be executed under the contract or any adjacent land, path, or street which may be allotted or used for the purpose of carrying our the contract.

x)	Normal time or stipulated time: Normal time or stipulated time means time specified in the work order to complete the work.

xi)	Extension of time: Extension of time means the time granted by the BSNL to complete the work beyond the normal time or stipulated time.

xii)	Date of commencement of work: Date of commencement of work means the date of actual commencement of work or 7th day from the date of issue of work order, whichever is earlier.

xiii)	Due date of completion: Due date of completion shall be the date by which the work shall be completed at site including clearance of site.

xiv)	Site Engineer: Site Engineer shall mean an SDE/SDO/JTO of the BSNL, Balangir who will be supervising the earthing  work on the site on behalf of  Telecom District Manager , Bolangir .

B)   INSTRUCTIONS TO BIDDER

- The Bidder is expected to examine all instructions, forms, terms & conditions and specifications in the bid documents. Failure to furnish all information required as per the bid document or submission of bids not substantially responsive to the Bid Documents in every respect will be at the bidder's risk and shall result in rejection of the bid.

- Tenders bidding for work should have appropriate resources, necessary expertise, requisite 	manpower, proper co-    coordinating and supervisory ability to undertake the work.

- This tender is meant  for carrying out the work for a period of one year only. The period of the validity 	of the work may be extended  for upto another six months as per the terms and conditions 	mentioned in this document, if required by the TDM, Bolangir and agreed by the contractor.

- The successful tenderer will have to execute the job to the satisfaction of the BSNL authority. Any deficiency in work can be computed by the concerned officer of the BSNL & the expense borne towards the work will be charged against the contractor as a penalty.

- The conditional and incomplete tenders are liable for rejection.

- Tenders without EMD will be rejected outright.

- The bidder whose relatives i.e., Wife, Husband, Parents, Grandparents, Children, Grand children, Brothers, Sisters, In-laws, Uncles, Aunts, Cousins and their corresponding in-laws working in BSNL are not eligible to participate in the Tender.

### SECTION – II

GENERAL TERMS AND CONDITIONS

1.	SCOPE OF  WORK		 :

The equipment earthing work is to be carried out for the different telephone exchanges and BTS premises under the jurisdiction of Telecom District Manager, Bolangir.

It involves:

- digging   of the earth pit of size lenth-3mx breadth-3m and depth not less than 4.5m., removing of the excavated soils  to distance places from the exchange by means of transportation  and the transportation charges will be borne by the contractor. If required the dewatering also will be done by the contractor.

- Supplying  and  fixing of earth plate of  size 600mmX600mmX6mm  and interconnecting the plates with each other by copper strip   inside the pit as per diagram .

- Supplying of copper  strips of size 25mmX3mm

- Fixing of earth conductor (copper strip ) from earth plate to the earth collector(Bus bar) inside the exchange / BTS.

- Fixing of GI pipe at the centre of the pit as per specification  for watering .

- Supplying  and  filling the earth pit alternately by charcoal and finely sieved good quality soil/black soil as per specification.

- Supplying and fixing of earth collector (Bus bar) of size 12’X4”X6mm on the Switch room/MDF.

- Making  chamber on the top of the earth pit as per specification  for watering the earth whenever required.

The G.I Pipe required for the watering purpose will be supplied by BSNL.

The  contractor has to supply the following items  for each  pit:

- Four nos. of copper plate  of size 600mmX600mmX6mm

- Copper Strip of size 25mmX3mm

- Charcoal  -17.55 CUM

- Finely sieved good quality soil  -22.95 CUM

- Copper Bus bar of size 12’X4”X6mm-one no.

- Required no. of Brass nuts and bolts

2.	BID  VALIDITY 	 :

The Bid will remain valid for a period of 120 days from the date of opening.

3.	QUERIES ON BID DOCUMENTS:

A prospective bidder, requiring any clarification on  the Bid Documents shall notify BSNL in writing or by fax on BSNL's mailing address indicated in the invitation for Bids. BSNL shall respond in writing to any request for clarification of the Bid Documents, which it receives not later than 7 days prior to the date for the opening of the bids. Copies of the query (without identifying the source) and the clarifications by BSNL shall be sent to all the prospective bidders who have purchased the bid documents and all such clarifications issued by BSNL will form part of the bid document.

4.	AMENDMENT OF BID DOCUMENTS:

- At any time prior to the date for submission of bids, BSNL may, for any reason whether suo motto or in response to a clarification requested by a prospective Bidder, modify the bid documents by amendments.

- The amendments shall be notified in the leading news paper or by Post or FAX to all prospective bidders on the     address intimated at the time of purchase of bid document from BSNL and these amendments will be binding on them.

- In order to afford prospective bidders reasonable time to take the amendments into account in preparing their bids, BSNL may, at its discretion, extend the deadline for the submission/opening of bids suitably.

3.	 PREPARATION & SUBMISSION  OF  BID	:

The tender will be a double bid system, i.e, Qualifying /Technical & Financial bid . One  envelope superscribed as “Technical Bid” will contain all  documents  as per clause-8 (A) of this section including EMD & the tender document duly signed on all pages by the bidder. It is to be sealed properly.

The second  envelope superscribed as “Financial Bid” will contain the quoted rate sheet only  as per Annexure-V & properly sealed. Rate should be quoted clearly both in figures and words. Rates quoted in words will be taken as the final rate as per rules. Any correction should be clearly scored out under proper attestation of the bidder.

A third envelope superscribed as “Tender for Carrying out Earthing  Works at different Telephone Exchanges  and BTS  premises in Bolangir  Telecom District ” will contain the above two envelopes and addressed to AGM (CM), First Floor .O/o Telecom District Manager, Door Sanchar Bhawan . Bolangir-767001. The tender may be dropped in the tender box available in the office chamber of AGM (CM), 1st Floor, O/o TDM, Bolangir before the stipulated date & time.

Tender Paper can also be submitted by Registered Post or through courier service. It will be the prime responsibility of the bidder for safe arrival of the tender document, if it is sent through Post or Courier. BSNL will not be responsible for any kind of late delivery or non-arrival of tender documents, sent through post or courier.

4.	QUANTUM OF  WORK 	:

The quantum of work is the tentative number of telephone exchanges and  BTS sites, for which the equipment earthing is to be done under different  field units of  Telecom District  Bolangir. However, the quantum of works may vary depending on the actual field requirements which will be decided by from time to time. The tentative list of exchanges and BTS for which earthing work is to be done is as follows:

| SL NO. | Name of SDCA | Name of SDE | Name of T.E./ BTS |
| --- | --- | --- | --- |
| 1 | Dungripali | SDE( NW OP Rural-CFA) Bolangir | Beheramal T.E |
| 2 |  |  | Nagaon T.E |
| 3 |  |  | Badtika BTS |
| 4 |  |  | Dungripali BTS |
| 5 |  |  | Singhijuba BTS |
| 6 |  |  | Badkarle BTS |
| 7 | Bolangir |  | Chhatamakhana T.E |
| 8 |  |  | Bileisarda BTS |
| 9 |  |  | Samara BTS |
| 10 |  |  | Badbandh BTS |
| 11 |  | SDE( NW OP City-CFA) Bolangir | Rly. Station, BGR BTS |
| 12 |  |  | Anand Nagar, BGR BTS |
| 13 | Birmaharajpur | SDE( NW OP Rural-CFA) Sonepur | Jaloi BTS |
| 14 |  |  | Mrusundhi BTS |
| 15 | Sonepur |  | Bausuni BTS |
| 16 |  |  | Badbhainro BTS |
| 17 | Titlagarh | SDE( NW OP Rural-CFA) Titlagarh | Bankel BTS |

The estimated cost of tender is about Rs.12,00,000/- (Rupees twelve lakh only).

5.	COST OF BIDDING	:

The bidder shall bear the cost associated with the preparation and submission of the bid. BSNL in no case will be responsible to bear these costs regardless of the conduct or outcome of the bidding process.

- BID PRICES:

    - The bidder shall give the total composite price inclusive of all levies and taxes of works and transportation costs  except    service tax.

    - The price quoted by the bidder shall remain fixed during the entire period of contract and shall not be  subject to variation on any account. A bid submitted with an adjustable price quotation will be treated as non responsive and will be rejected.

7.	BID SECURITY (EARNEST MONEY DEPOSIT)

7.1 	Earnest Money Deposit of Rs. 30,000/- (Rupees thirty  thousand only) is to be paid by each tenderer through a crossed Demand Draft / Bankers Cheque drawn on any nationalized bank/Scheduled bank in favour of Accounts Officer (Cash) BSNL, O/o TDM, Bolangir or Cash in form of ACG-67 to AO (Cash) O/o TDM, BSNL, Bolangir.

7.2. 	No interest is payable on the Earnest Money deposit. The Earnest Money deposit of unsuccessful tenderer will be refunded within reasonable time after final decision of the tender, normally within six months from the date of opening of tender.

7.3	Earnest Money deposit is liable to be forfeited in case if tenderer

a. Withdraws the tender offer before finalization of the same.

b. Fails to accept the offer when his/their tender is accepted.

c. Fails to pay the Security Deposit within the stipulated time.

d. Fails to execute the Agreement within stipulated time.

e. Fails to carry out the work within stipulated time limit.

8.	DOCUMENTS TO BE SUBMITTED ALONG WITH TENDER PAPER:

The following documents are to be submitted along with the tender document;

- Technical Bid  Documents

  - Attested copy of firm Registration certificate in case of firm.

  - Attested copy of Valid PAN Card.

  - Attested copy of Certificate of Registration with EPF authorities.

  - EMD Rs.30, 000/- in shape of DD from a scheduled Bank at Bolangir.

  - Money receipt/DD towards the cost of tender paper.

  - Experience certificate: - The contractor should have experience of having done the  earthling  work in BSNL/MTNL/State Govt./ Central Govt. or central  PSUs of amount not less than Rs 2, 00, 000/- (Rupees Two Lakhs) during last two FY 2008-09  and 2009-10. Experience certificate in this regard is to be issued by an officer not below the rank of Deputy General Manager or equivalent.

  - Power of attorney, if any, in respect of the authorized person on behalf of firm or contractor.

  - Technical Bid document in original duly filled in and signed by the tenderer alongwith  the seal on each page.

  - Attested copy of Service Tax Registration Certificate.

  - Attested copy of  Valid Labour License from the Central Labour Commission under Contract Labour Act 1970 (R&A) or undertaking to get it within one month from date of signing the agreement.

  - Valid Contractor License.

- Financial  BID Documents

- Financial Bid duly filled in as per Annexure-V.

All corrections and overwriting must be initialed with date by the tenderer or his authorized representatives.

NOTE :

-	Non submission of any one of the above document with the tender imply disqualification and   the tender will be rejected.

- 	Original Documents will be verified before signing of the agreement or at any time at the discretion of TDM, Bolangir.

- 	Attested copy means self attested.

9.	OPENING  OF  BID:		:

    - The Department shall open the bids in the presence of bidders or his authorized representative, on due date & time. The bidder or his representative, who is present, shall sign in attendance register. The bidder’s representative shall submit authority letter as per Annexure-IV, to this effect before they are allowed to participate in the bid opening.

  - Only one representative for any bidder shall be authorized and permitted to attend the bid opening.

    - The Bids shall be opened in the following manner:

    - The bid opening committee shall count the number of bids and assign serial numbers to the bids.

The bid opening committee shall sign on the envelope with date. First the Technical bid will be opened by the bid opening committee. Those who will qualify in the technical bid only their financial bid will be opened. The Financial bid will be either opened in the same date or on a later date which will be intimated to the concerned bidder by the opening committee.

    - The envelopes containing the tender offer and not properly sealed, shall not be opened and shall be rejected outright. Closing the cover by gum will not be treated as sealed cover. The reasons for not opening such tender offers shall be recorded on the face of the envelope and all the members of bid opening committee shall put initial with date.

9.4   	Postponement of Tender opening: Whenever it is considered necessary to postpone the opening date of tenders, quick decision must be taken and communicated to the tenderers who have purchased the tender documents and shall be at least one day before the original date of opening. If the date of opening of bids is declared as holiday, or any bandh occurs then the bids will be opened on the next working date at the same time and venue.

The BSNL if subsequently declares date fixed for opening of bids as holiday, the revised schedule will be notified.  However, in absence of such notification, the-bids will be opened on next working day, time and venue remaining unaltered.

10.	SELECTION OF BID

10.1.   The Lowest (L1) bidder  will be selected by  comparing the rate quoted at serial    number  01  (one) to Serial No-10  of the financial bid. Total lowest from Sl. No one(1) to ten(10) will be taken as L1.

    - The rates are to be quoted both in words and figures. If there is a discrepancy between words and figures,  the rate quoted in words shall be taken into consideration. Prior to detailed evaluation, the BSNL authority will determine the substantial responsiveness of each bid to the documents. A substantially responsive bid is one which conforms to all the terms and conditions of bid documents without material deviation. A bid determined as substantially non-responsive will be rejected.

11.	SIGNING OF CONTRACT	:

The successful tender shall be required to execute an agreement on a non judicial stamp paper of Rs.50/- only at his own cost as per the enclosed proforma in Annexure-II. Before signing  the agreement , the bidder will have to deposit the  Performance Security Deposit  as per clause  no.13  of  this section of the tender document. In the event of failure on  the part of the tenderer  to sign the agreement within seven(7) days of being called upon to do so after the acceptance of the tender, or in the event of his failure to start the work as stipulated, the amount of earnest money deposit or performance security shall be forfeited by BSNL and the acceptance of the tender shall be considered as revoked.

12.   ALLOTMENT OF WORK:

The TDM, Bolangir  reserves the right either to allot the whole work to L1 bidder or to distribute the  work between L1 and L2  in the ratio of  65:35  percentage  provided the L2  bidder agrees to execute the work  at L1 rate and other terms and conditions remaining  the same. The distribution of work depends on the quantum of total work at the time of awarding the work, but the decision entirely lies with the TDM, Bolangir.

13.	PERFORMANCE  SECURITY 	:

  - The successful bidder shall be required to deposit  performance Bank Guarantee @10% of the estimated cost i.e. Rs.1,00, 000/-

  - Performance security has to be submitted in the form of Bank Guarantee issued by any scheduled Bank at Bolangir valid for a period of 18 months.

  - Performance security will be discharged after completion of contractor’s performance obligations under the contract without interest means it will be released only after expiry of the warranty period

  - If the contractor fails or neglects any of this obligations under the contract either whole or part of performance security furnished by the bidder shall be forfeited to BSNL as compensation for any loss resulting from such failure.

e.      The Performance Security Deposit (SD) is required to protect the BSNL against the risk of bidders performance and will be forfeited as part / whole in case of -:

i).Unsatisfactory performance.

ii).Damage caused to BSNL assets and damage/loss of store issued

iii).Withdrawal of the successful tenderer  from the contract before its expiry without giving proper notice as specified in the terms & conditions of this tender document.

f).      The Performance Security deposit shall be released/refunded within 120 days from the date of the payment of     the last final bill of the work under the contract and final settlement of material account on production of “no dues certificate” from “Engineer-in-charge”.

- PRICE VARIATION :

The BSNL shall not be responsible for any escalation of wages  of labor or materials, machinery,   equipment etc., whatsoever or any increase in any duties levies or taxes, in respect of whatsoever and the contractor’s rates and contractor’s obligation shall remain unaltered by such escalation. The contract price will remain fixed for the duration of the contract. But contractor is required to pay to the laborers engaged by him  as per the minimum rates fixed by the central Labour Commissioner from time to time . BSNL in no way will be responsible for paying the contractor for hike in labor rates.

- SUBCONTRACT

The contractor shall not assign, subcontract or sublet the whole or any part of the work covered by the contract. Incase it is proved that the tenderer has engaged subcontractors,  the tender awarded in his favour would be treated as null and void and SD will be forfeited.

- LABOUR WELFARE MEASURES  & WORKMAN COMPENSATION :-

- The contractor should have valid labour license under the Contract Labour (R & A) Act 1970 and the Contract Labour (Regulation and Abolition) Central Rules 1971 and should abide by the requirements of such act.

- The contractor shall comply with all provisions of the ‘Payment of wages Act’ 1936, minimum wages Act 1948, Employees liability Act 1938, Workmen compensation Act 	1923, Maternity benefit Act 1961 and contractor labour (Regulation and abolition) Act 1970 or the modifications thereof or any other laws 	relating thereto and the rules made there under from time to time. The contractor shall 	indemnify BSNL against payments to be made for the observance of the laws aforesaid.

- All the amenities to the laborers such as drinking water, washing facilities should be provided by the contractor at his own cost at the work spot as required under Contract Labour (R &A) Act, 1970.

- The contractor shall be responsible for and shall pay any compensation to his workmen payable under the workmen’s compensation Act, 1992 for injuries caused to the 	workmen. If such compensation is paid by the BSNL as principal employer under Section (1) of the Section 12 of the said Act, such compensation will be recovered from the security deposit or any account due from the contractor on any account or otherwise.

- The contactor will be responsible for the safety and security to the skilled and unskilled labors employed by him for execution of work.

- The tenderer will observe necessary formalities as per the provision of the labor  act & BSNL will not in any way be responsible for any breach of labor act or any cases relating to labor and employment. However the following points may be implemented.

- However the contractor should follow the following points positively:

- Muster roll has to be maintained in respect of laborers engaged by the contractor with weekly offs to the laborers as admissible.

- The copy of Paid Challan of EPF/ ESI/ Service Tax of Previous month should be submitted along with the Bill.

- The payment of contract laborers by the contractor is to be carried out as per the rate approved by the Central Govt. from time to time for skilled/unskilled worker category.

- The contract  laborers engaged by the contractor are to be covered under ESI and EPF scheme by the contractor himself as per rules, positively.

- The contractor will issue employment cards to engaged contract laborers.

- The contractor should furnish its personal information along with contact telephone number both landline and mobile and should always be available for contacting to take work orders.

17.	TERMINATION OF CONTRACT:

  - Under the following conditions the competent authority may rescind/terminate the contract

    - If the contractor suspends the execution of work & the engineer in charge of the work comes to  judgment that the work could not be completed by the due date for completion or the contractor had already failed to complete the work by that date.

    - If the contractor who had been given by the officer in charge of  work a notice in writing to rectify/replace any defective work fails to comply with the requirement within a period of seven days from the date of receipt of such notice

    - If the contractor commits breach of any item of conditions in the contract or sublets without prior permission, the Engineer in charge of the work can determine or rescind the contract. Before determining/rescinding, the Engineer in charge shall give first show cause notice .Thereafter Notice on Final Action will have to be served in case no response is received for first show cause notice.

  - Termination on Insolvency:

BSNL may also by giving written notice and  without compensation to the contractor terminate the contract if the contractor becomes unwilling, bankrupt or otherwise in any way without affecting the right of action or remedy as hirer.

- Force majeure :

If any time, during the continuance of this contract, the performance in whole or in part by either party of any obligation under this contract is prevented or delayed by reason of any war of hostility, acts of the public enemy, civil commotion, sabotage, fires, floods, explosions, epidemics, quarantine restrictions, strikes, lockouts or act of God (Herein after referred to as events) provided notice of happenings, of any such eventuality is given by either party to the other within 21 days from the date of occurrence thereof, neither party shall by reasons such events be entitled to terminate this contract nor shall either party have any claim for damages against the other in respect of such on performance or delay in performance under the contract shall be resumed as soon as practicable after such an event may come to an end or cease to exit, and conclusive, provided further that if the performance in whole part of any obligation under this contract is prevented or delayed by reason of any such event for a period exceeding 60 days either party may, at his option terminate the contract.

19.  ARBITRATION :

- In the event of any question, dispute or difference arising under the agreement or in connection there-with (except as to matter the decision to which specifically provided under this agreement), the same shall be referred to sole arbitration of the TDM, BSNL, Bolangir. In case his designation is changed or his office is abolished then in such case to the sole arbitration of the officer for the time being entrusted whether in addition to the function of the TDM, Bolangir or by whatever designation such officer may be called (herein after referred to as the said officer) and if the TDM, Bolangir or the said officer is unable or unwilling to act as such, then to the sole arbitration of some other person appointed by the TDM or the said officer. The agreement to appoint an arbitrator will be in accordance with the Arbitration and Conciliation Act, 1996.

- The arbitrator may from time to time, with the consent of both the parties extend the time frame for making and publishing the award. Subject to aforesaid arbitration and conciliation Act, 1996 and the rules made there-under, any modification thereof for the time being in force shall be deemed to apply to the arbitration proceeding under this clause.

- The venue of the arbitration proceeding shall be O/o TDM, BSNL, Doorsanchar Bhawan, Bolangir or such other place as the arbitrator may decide.

20.	SET OFF	:

Any such of money due and payable to the contractor (including security deposit refundable to him) under this contract may be appropriated by BSNL and set off the same against any claim of BSNL for payment of the sum of money arising out of this contract or under any other contract with BSNL.

21.	PAYMENT TERMS AND CONDITIONS:

21.1  	Payment for execution of earthing  work will be made by BSNL only after satisfactory completion of the work as per the specification  subject to the issue of the certificate from the SDE concerned regarding satisfactory completion of the work duly countersigned by the DE concerned and after acceptance of A/T. No payment for incomplete works will be considered.

21.2   The contractor may submit bills in duplicate along with (i)Work Order,(ii) Material Account statement and (iii) MB based on the joint measurements recorded in the M.B. and signed by the contractor, SDE concerned in each page of the M.B. The M.B. must contain the dates of commencement and completion of the work and other particulars of the work in details. The bill must be countersigned by concern DE.

21.3  . 90% payment will be done after production of bill as per clause 21.2 above and rest 10% will be paid after one year from the date of clearance of A/T .

21.4    Payment will be made through E-Payment or cheque. For E-Payment the contractor will have to  furnish the Union Bank  of India  A/c No. (Core banking) in the front of bill.

21.5     Income tax and other taxes if any will be recovered from each bill submitted by the contractor. This is subject to change as and when required under statutory rules. However the service tax and cess (If required) will be charged extra by the contractor at the time of producing bills.

21.6    For the purpose of claiming of service tax by the contractor and to enable availing of credit to that extent by BSNL, the contractor shall prefer bills in triplicate, having printed bill No, printed service tax Regn No. PAN No. etc. The component of service tax & education cess and higher education cess shall be shown separately.

21.7   The contractor has to submit the bill compulsorily  within one month from the date of completion of work along the A/T clearance report  otherwise the bills  will not be considered for payment.

21.8    The Security Deposit submitted by the contractor will be refunded  only after the  warranty period is over

22.	OTHER TERMS & CONDITIONS:

  - Tender quoted with unworkable rates will be rejected.

  - TDM, Bolangir reserves the right to accept or cancel any or all the tenders without assigning any reason thereof and is not bound to accept the lowest rate.

  - In case of any dispute the decision of the TDM, Bolangir is final and binding.

  - The tenderer will observe necessary formalities as per the provision of the Labour Act and the TDM, Bolangir will not in any way be responsible for any breach of Labour Act or any such cases relating to labour & employment. The contractor will also be held responsible for any damage/loss caused to BSNL by his employee and such loss will be recouped from the contractor.

  - The Telecom District Manager, Bolangir reserves the right to disqualify such bidders who have a record of not meeting the contractual obligations against earlier contracts entered with the B.S.N.L

  - The TDM Bolangir reserves the right to increase or decrease the duration-and validity of the contract from normal one-year duration in the interest of the B.S.N.L. Bolangir

  - In case of any dispute, case would be referred to the Telecom District Manager, Bolangir or any other authority looking after the duties/works of Telecom District Manager, Bolangir and he would be the sole arbitrator. His decision would be final and binding on all cases.

23. PENALTY  CLAUSE:

For delays in the contractor’s performance, the following actions will be taken:

  - The time allowed for completion of work as entered in the work order shall be strictly adhered to by the contractor and shall be reckoned maximum from the seventh day from the issue of the work order by BSNL. The contractor shall pay as penalty amount equal to 1 % of the amount of the incomplete work for every one week of delay in completion of work subject to a maximum of 10 % of the cost of the work awarded.

  - On any date the penalty payable as above reaches 10 % of the estimated cost of the work , the contractor should proceed with the work further only on getting a written instruction from the concerned DE, that, he is allowed to proceed further with the work..

  - Penalty for delay in completion in work shall be recoverable from the bill of the contractor and/or by adjustment from the SD or from the bill of any other contract. However adjustment from SD will be made only when the contract has been terminated or at the time of final settlement of bills on completion of work.

24.	NEAR RELATIVE

(i)	The contractor shall not be permitted to participate in the tender if any of his near relative is working as an officer or official in any capacity in Bharat Sanchar Nigam Limited. He should submit a declaration that, no his/her near relative is employed in Bharat Sanchar Nigam Limited as per  ANNEXURE-III.

(ii)	By the term 'near relative' is meant wife, husband, parents and grand parents, children and grand children, brother and sister, uncles and aunts and cousins and their corresponding in-laws.

- The bidder should give a declaration that none of his/her near relative is working in the units as defined below where he is going to apply for the tender. In case of proprietorship firm certificate will be given by the proprietor. For partnership firm certificate will be given by all the partners and in case of limited company by all the Directors of the company excluding Government of India / Financial institution nominees and independent non-official part time Directors appointed by Govt. of India or Governor of the state. Due to any breach of these conditions by the company or firm or any other person the tender will be cancelled Bid Security will be forfeited at any stage whenever it is noticed and BSNL will not pay any damage to the company or firm or the concerned person.

The company or firm or the person will also be debarred for further participation in the   concerned   Unit.

The near relatives for this purpose are defined as:-

  - Members of a Hindu undivided family.

  - They are husband and wife.

  - The one is related to the other in the manner as father, mother, son(s) & Son’s wife ( daughter in law), Daughter(s) and daughter’s husband ( son in law), brother(s) and brother’s wife,` sister(s) and sister’s husband ( brother in law).

25.    WARRANTY:

The contractor would  provide a  warranty of two year on the earth value   from the date of  commissioning of the  earth . Within the warranty period  the contractor  has to ensure that the earth value should  be within the limit i.e.,  0.5 Ohm.  If at any time it is found that the earth value  is more than  0.5 Ohm, then the contractor would  do  the necessary  rectification  work   so as to bring the  earth value within the limit.  Rectification work  will be done by the contractor at its own cost.  Normally this work should be completed within one month time. If the contractor fails to perform, then the rectification work will be done either by  separate contractor or departmentally as decided by the authority . The cost  incurred , will be recovered from the  contractor’s  security deposit (SD).

26. TECHNICAL SPECIFICATIONS:

Earth system employed in a building accommodating  exchange  or BTS will consist of following parts.

EARTH ELECTRODES

EARTH CONDUCTOR

EARTH COLLECTORS.

Earthing here means- termination of earth from pit to earth collector. Resistive value of earth at the point of termination on earth collector should be less than 0.5Ohm. Pit type earth indicated in NIT for tender means type of earth made with electrode consisting of copper plates of size (600 x 600 x 6 mm) buried in the soil at the depth ranging from 12ft onward.

The copper earth plates, strips, etc should be electrolytically pure copper conforming to latest ISI specifications .  If  it  is found that copper plates are having any impurities, then the entire security deposit/EMD shall be forfeited and the contractor  will be black listed. The guage  and size have to be maintained strictly and shall be checked by the concerned DE before execution/supply to the BSNL. The tenderer shall give two  year warranty on execution of work/ supply of copper items and GI pipes from the date of successful commissioning of the earth. The SDO Incharge will take the approval of the concerned D.E showing visible marker laid over the    earth electrodes and conductors system, depth of pit, distribution of earth showing different locations from earth collector (earth busbar). Necessary sanction of related detailed estimate may be taken from this office.

26.1    Earth pit:

Normal size of the earth pit should  be 3mt  length X 3mt. breadth . The depth should not be less than 4.5mtr.  and maximum limit will be determined by local condition of the pit selected under consultation with work incharge. There should not be any compromise on the depth of earth pit, the minimum size as per above has to be maintained by the contractor. The SDE incharge should verify the pit himself personally before allowing the contractor to work further.

26.2.  EARTH ELECTRODES :

It will consist of four copper plates of size 600x600x6 mm each and shall be arranged vertically  on the edge at  four corners of the pit  as shown in figure 1.These four plates are to be placed  diagonally opposite  to each other with a gap of  minimum 1ft. from the  pit wall . These four  plates are to be placed  at  a height  of 60cm from the  bottom of the pit after filling this  gap with   finely sieved good quality loose  soil or black soil  as  shown in the  fig-5  in consultation with the  work incharge.

26.2.1  Connection of Earth Electrodes/Plates :

All four copper plates in side the earth pit are to be inter-connected with each other by copper flats  /strips of  size  25mm width x 3mm thickness in a continuous  loop  as well as  in diagonally  to each other   as shown in the  fig-1 and 2.  The copper plates and strips are to be  connected  and tightened with each other  by brass nuts and bolts  of appropriate  size along with brass washers  as shown in the  fig-3 .  While  making  the  contact between plate and  strip , it must be ensured by the contractor  that two nos  of holes  should be  made   on both  the plate  and strip for better Ohmic contact. The nuts and bolts are to be tightened firmly. To prevent ingress of moisture and soil, the joint should be made water tight by covering with bitumen.

26.3   EARTH CONDUCTOR :

The earth conductor is the copper strips of size 25mm width x 3mm thickness.  Two nos of  earth conductors  of above  size  are  to be  connected  from  two diagonally opposite  earth  electrodes (Copper Plates)  as per  fig-3 and are to be extended  from the earth pit to the  earth collector  fixed in the equipment  room/ MDF as shown in the fig-1.  The two nos of earth conductors after taking from the earth  pit . are  to be fastened with the G.I. pipe  kept for watering the earth , by copper wire at 2ft apart and will be taken out from the G.I. pipe  to  the  nearest point of the  earth bus bar.  The strips  are to be  carried via a  trench  with a depth of 4ft  from the ground  surface,  the copper strips are to be laid  inside a  GI pipe of  appropriate  length and  diameter to the  earth distribution  point  or Copper  bus bar .  These  two ends  are to  be  connected  with the  bus bar  by  brass nut and bolts of  10 mm holes with two brass washers . While laying the earth conductor from  earth pit to the  busbar , it must be strictly ensured by the contractor  that the  copper strips  should not have any joints . The bends in Cu strip should not be sharp but with a radius of one meter

26.4    EARTH COLLECTORS :

Earth distribution plate/ earth bus bar at MDF or  Switch room will act as earth collector and thus contractor will provide earth distribution plate  which  will be  a pure copper of   size (12``x4``x 6 mm) and this has to be   fixed over the wall  firmly  at  a height  of  30cm from  floor level  with  bakelite sheet with fiber insulators fixed on wall with arrangement as indicated in figure- 4. It should have minimum six nos. of equally spaced holes of 10mm diameter over it.

For any further clarification if needed can be seen from engineering instruction no-E-1002 and I-001 but decision of SSA will be final in terms of above details prescribed herein.The contractor will be required to exhibit an earth resistance of less than 0.5 Ohm. Higher resistance will not be acceptable.

26.5   Filling up of the pit:

The earth pit is to be filled up with soft soil and charcoal in layer by layer alternately up to the ground level as per fig-5 enclosed with this tender document. The first  60cm  depth from the  bottom of the pit is to be filled by   finely sieved good  quality  soil preferably black soil  which should be rammed in layers so that it is compact and cohesive and then next 65cm depth by charcoal  and next 65cm by loose soil  and so on  as shown in the fig-5. Each layer is to be watered and rammed so that it is compact and cohesive. The remnants around the earth pit are to be cleaned properly. The refilling activity should be supervised by an officer not below the rank of JTO.

26.6   Watering Arrangement:

Watering arrangement will be done by providing GI Pipe of 5mt. length and 2 inches dia, grade –B from the centre of bottom of the pit to the surface of the ground for pouring water as shown in Fig. No-1.  One funnel of appropriate size has to be provided on the top of the GI pipe for pouring water into the pit.  The funnel and the GI pipe  are to b e protected on the  ground surface in  a cement brick  chamber  with inside  dimension of  1ft X 1ft. size  with  a  small  cast iron cover  on the top of the funnel in order to protect the  mouth of the funnel  from blocking  by dust or soil etc. The value of earth resistance should be less than 0.5 Ohms. The job should be duly acceptance tested by the A/T officer authorized by TDM-Bolangir.

27.   NOTE: ( Instructions to Contractor)

The total earthing work is to be directly supervised  by SDE incharge himself  . All the copper materials and G.I. pipes are to be first examined by the concerned Divisional Engineer himself as whether the materials are confirming to the specification given in the tender document. After getting the  OK certificate only, the contractor can  proceed for work. Similarly the trench has to be verified for its tech. specifications by the SDE/DE before further proceeding to work by the contractor.  Sameway  the refilling activity should be  supervised by an officer not below the rank of JTO /SDE. The contractors have to take utmost care and precautions to execute the work as per technical specification laid in clause no 26. Any deviation found will be taken seriously and the work order issued will be cancelled, SD/EMD etc will be forfeited, and the contractor will be barred from participating in any of the contractual work under the SSA.

Payment will be made if the ohmic value of the earth is 0.5 ohms or less, otherwise the payment will be held up till rectification and bringing down the earth value ≤0.5 ohms.

28.  SCHEMATIC  DIAGRAM OF EXCHANGE EARTHING

To Switch Room or MDF

3 mt.

G.I. Pipe with

Funnel for Watering purpose

(Length-15m, Dia.-2 inch)

4.5mt

Copper Plate

(Size 600mmX600mmX6mm)

Fi

Copper  Strip

(Size  25mm X 3mm)

3 mt.

Fig.  - 1

1ft

1ft

Copper Plate

(Size  600mmX600mmX6mm)

3mt.

Fig.- 2  (Plan View)

(Diagram not to Scale)

3mt.

Copper Plate

Copper Strip

Copper Plate & Strip Jointing System

( Jointing to be done by Brass Nots ,

Bolts & washers)

Fig. 3    Copper Plate & Strip Joint (Diagram not to Scale)

12 inch

6mm

4          4            4 inch

Copper Bus bar

Copper Strip from Earth Pit

Fig.   4  ( Earth Collector/ Bus bar)

Finely  sieved good quality Soil   65cm

Charcoal                           65cm

Finely  sieved good quality Soil   65cm

4.5mtr.  	           Charcoal                           65cm

Finely  sieved good quality Soil    65cm

Charcoal                            65cm

Finely  sieved good quality Soil    60cm

Fig.  5   (Earth Pit Refilling System)

ANNEXURE – II

FORMAT OF AGREEMENT

The agreement made on this ________________day of (month) _________ (year) _________ between __________________________________________, herein after called “The Contractor” (Which expression shall unless excluded by or repugnant to the context, include its successors, he executors, administrative representative and assignee) of the one part & Bharat Sanchar Nigam Limited,  a  Govt. of India Enterprise having its one field office  at Bolangir  headed by the  Telecom  District  Manager,  here in after referred to as TDM, Bolangir, on other part.

Where as the contractor has offered to enter into contract with BSNL, Bolangir  for the execution of “Carrying out the Earthing  Works at different Exchanges and BTS premises in Bolangir Telecom District” terms and conditions herein contained in the tender document and the rates approved by the TDM, Bolangir  (copy of Rates annexed) have been duly accepted and where as the necessary security deposits have been furnished in accordance with the provisions of the tender document and whereas no interest will be claimed on the security deposits.

Now these presents witness and it is hereby agreed and declared by and between the parties to these presents as follows;

1)This contract , will normally remain valid for a period of one year  from the date of agreement  i.e., _________________.  The contract  can be  extended  for  a further period  of  six months or until this contract shall be terminated by such notice as is hereinafter mentioned.

- The contractor  agrees that, the work is to be  carried out by means of labors employed  by the contractor at his own expenses and by means of tools, implements and equipment etc. to be supplied by him to his labor at his own expenses and all works are to be executed  as per the technical specification  described in tender documents  in consultation with the work incharge. It is understood by the contractor that the quantity of work mentioned on the schedule is likely to change as per actual requirements as demanded by exigencies of service.

3)	The NIT (notice inviting tender), Bid document (Qualifying and Financial), letter of intent, approved rates, annexed hereto and such other additional particulars, instructions, work orders as may be found requisite to be given during execution of the work shall be deemed and taken to be an integral part of the contract and shall also be deemed to be included in the expression “The Agreement” or “The Contract” wherever herein used.

4)	The contractor hereby declares that nobody connected with him is  in the employment of BSNL, he  is not/shall not ever be admitted as partner in the contract.

5)	The contractor shall abide by the terms and conditions, rules, guidelines, construction practices, safety precautions etc. stipulated in the tender document  including any correspondence between the contractor and the BSNL having bearing on execution of work and payments to the labor engaged  by the contractor for execution of  work will  be done as per minimum wages fixed by the Central Govt. from time to time under the contract.

6)	Whereas the contractor agrees that he will provide  a warranty of two years on the earth value i.e., the earth value should be less than or equal to 0.5 Ohm.

7)	The contractor agrees that the contract can be terminated at any time  by the TDM, Bolangir due to bad quality of work or delay in execution of work  as per the tender conditions .

8)	The contractor also agrees that the A/T clearance will be done by him after completion of work.

5)	Performance Security of  Rs.1.20,000/- in terms of Bank Guarantee dated………………….. has been deposited by the contractor.

In witness whereof the parties presents have here into set their respective hands and seals the _____ day of (month) __________ (year) __________.

Signature of							Signed & Delivered on behalf

Contractor/Firm 				                    	      of the BSNL, Bolangir

Witness Signature from Contractor 				Witness from BSNL

Name :								Signature :

Address : 							Name :													Address :

ANNEXURE-III

DECLARATION OF NO NEAR RELATIVE WORKING IN BSNL

I ………………………………………………………. S/o………………….. ………………………………………….Address ……………………………………………….. …………………………………………………………………….. hereby declare that none of my relative (s) as defined below is/are employed in BSNL unit as per details given in tender document. In case at any stage, if it is found that the information given by me is false/incorrect, BSNL shall have the absolute right to take any action as deemed fit/without any prior intimation to me.

(i)	The near relatives for this purpose are defined as:

(a)	Members of a Hindu Undivided family,

(b)	They are husband and wife,

(c)	The one is related to the other in the manner as father, mother, son(s) & son's wife (daughter-in-law), Daughter (s) & daughter's husband (son-in-law), brother (s) & brother's wife, sister (s) & sister's husband (brother-in-law).

Signature of Bidder with seal

ANNEXURE-IV

LETTER OF AUTHORISATION FOR ATTENDING BID OPENING

Tender Number...........................................................................................................................

Subject : Authorization  for attending bid opening on ........................................ (date) in the tender of ..........................................................................................................................

Following persons are hereby authorized to attend the bid opening for the tender mentioned above on behalf of ..............................................................................................................…………... ………………………………………………………………………………………….

(Bidder) in order of preference given below .

Order of Preference 			Name			Specimen Signatures

I

II

Alternate

Representative

Signature of bidder

or

Officer authorised to sign the bid

documents on behalf of the bidder.

No.     1.	Maximum of two representatives will be permitted to attend bid opening. In cases where it is restricted to one, first preference will be allowed. Alternate representative will be permitted when regular representatives are not able to attend.

- Permission for entry to the hall where bids are opened may be refused in case authorization as prescribed above is not produced.

TENDER FOR CARRYING OUT EARTHING WORKS IN DIFFERENT T.E. & BTS PREMISES OF BOLANGIR TELECOM DISTRICT

To

The Assistant General Manager (CM),

O/o the Telecom District Manager, Bolangir

Sub:  Rate Quotation for the tender  “Carrying out  the Earthing  works in different  Telephone Exchanges & BTS premises of  Bolangir Telecom District, Tender Notice No : NIT No: W-78/10-11/08 Dated at Bolangir on the 16th June, 2010.

Sir,

With reference to your Tender Notice cited above. I/We do hereby quote the rates for the tender “Carrying out  the Earthing  works in different  Telephone Exchanges & BTS premises of  Bolangir Telecom District,” and do hereby agree to the terms and conditions of the tender mentioned in the notice. The rates are quoted are inclusive of all taxes and transportation charges:

If our Bid is accepted, we shall submit the securities as per the conditions mentioned in the contract. We do agree to abide by this Bid for a period of 120 days from the date of opening of the bid and it shall remain binding upon us and may be accepted at any time before the expiry of that period.

Name of the Firm/ Bidder:

Address:

Dated:-……./……./……….

Place:

##### ANNEXURE-V

### FINANCIAL BID

Details of Item and quantity of work for making earthlings at 17 sites in

Bolangir SSA

| Sl.No. | Schedule of work | Unit | Rate in figures | Rate in Words |
| --- | --- | --- | --- | --- |
| 1 | Digging of earth pit of size 3M X 3M X 4.5M of depth irrespective of any soil . | Per pit |  |  |
| 2 | Supplying finely sieved good quality soil for filling the earth pit | Per CUM# |  |  |
| 3 | Supplying Charcoal for the earth pit | Per Bag* |  |  |
| 4 | Charges for filling up the earth pit with finely sieved good quality soil, char coal and mixture in layer by layer upto the surface level as per the Fig.-5 and also as per instructions of JTO/SDE concerned | Per Pit |  |  |
| 5 | Removal of excavated soil from the site or spreading inside the compound as per direction of BSNL official/officer | Per Pit |  |  |
| 6 | Supply and fixing of copper plate of size 600mmX600mmX6 mm thickness | Per Plate |  |  |
| 7 | Supply of Copper Strip/ Flat of size 25mmX3mm | Per metre |  |  |
| 8 | Fixing of Copper Strips ( from Plate to plate within the earth pit & from plate to the earth Bus bar along with making holes on the plate and strip and supplying required number of brass nuts , bolts and washers) | Per metre |  |  |
| 9 | Charges for making cement brick chamber over the earth pit and surrounding the GI pipe for pouring water into the earth pit | Per Pit. |  |  |
| 10 | Supplying and fixing of Copper Bus bar of size 30cmX5cm and thickness 6mm along with six nos. of spare holes of 10mm diameter as per fig-4 | Per Busbar |  |  |

*Bag means standard 50kg cement carrying bag

# CUM means Cubic Metre (i.e, 1mX1mX1m)

NOTE :

- The rates to be quoted should be inclusive of all taxes & transportation charges. Service tax will be paid extra by BSNL as per rule.

Signature of the bidder

With full address

Contact Telephone No:

Mobile/FAX No:

CHECK LIST

A.	TECHNICAL BID DOCUMENTS

1.     Attested copy of firm Registration certificate in case of firm.

2.     Attested copy of Valid PAN Card.

- Attested copy of Certificate of Registration with EPF authorities.

- EMD Rs.30, 000/- in shape of DD from a scheduled Bank at Bolangir.

- Money receipt/DD towards the cost of tender paper.

- Experience certificate: - The contractor should have experience of having done the  earthing  work in BSNL/MTNL/State Govt./ Central Govt. or central  PSUs of amount not less than Rs 2, 00, 000/- (Rupees Two Lakhs) during last two FY 2008-09  and 2009-10. Experience certificate in this regard is to be issued by an officer not below the rank of Deputy General Manager or equivalent.

- Power of attorney, if any, in respect of the authorized person on behalf of firm or contractor.

- Technical Bid document in original duly filled in and signed by  the tenderer alongwith  the seal on each page.

- Attested copy of Service Tax Registration Certificate.

- Attested copy of  Valid Labour License from the Central Labour Commission under Contract Labour Act 1970 (R&A) or undertaking to get it within one month from date of signing the agreement.

- Valid Contractor License.

B. 	FINANCIAL BID  DOCUMENTS

- Financial Bid duly filled in as per Annexure-V.

# Text boxes

Cost of Tender Paper Rs.520/-

Tender Document No.

RECEIPT OF THE TENDER PAPER- UP TO 13.00 HRS ON DATED 02/07/2010

###### OPENING OF TENDER PAPER AT 16.00 HRS ON DATED 02/07/2010

Space for Photograph

4.5mt.